## Register address
REV 3 | Control Techniques
| The Modbus register sometimes has a offset of 1 depending on the HMI and drive combination used. |  |  |  |  | Enter Modified Address to calculate drive Menu and Parameter
To get the modbus register just enter the parameter and menu values in the blanks below.
| Our drive has two different modbus formats. Standard and Modified. We also support 16 and 32 bit register over modbus. |  |  |  |  | Modified 32bit Protocol Register | 5.0078
| All 32 bit parameter can be called as 16 bit registers, this just limits the max value that can be retrieved. |  |  |  |  | 17666 | 0.0078125
| By default the drives are setup to use standard and this is the most used format. |  |  |  |  | Menu | Parameter
[5 empty] | 20993 | 5.0078 | 0.003
|  | Edit value below | Edit value below
| Mode | Menu | Parameter | Modbus register | Protocol register
| Standard 16 bit reg | 6 | 34 | 400634 | 633
| Modified 16 bit reg |  |  | 401570 | 1569 | Enter Modified Address to calculate drive Menu and Parameter
| Standard 32 bit reg |  |  | 417018 | 17017 |  | 17667
| Modified 32 bit reg |  |  | 417954 | 17953 | Modified 32bit Modbus Register | 5.0117
[6 empty] | 417667 | 0.011719
[6 empty] | Menu | Parameter
| How the math works mm is the menu and ppp is the parameter in the menu |  |  |  |  | 5.0117 | 0.003
| CT Parameter | Modbus register |  | Protocol register
| s.mm.ppp | Standard | 40000 + mm * 100 + ppp | mm * 100 + ppp - 1
|  | Modified | 40000 + mm * 256 + ppp | mm * 256 + ppp - 1
Examples
| 0.1.021 | Standard | 40121 | 120
|  | Modified | 40277 | 276
| 0.1.000 | Standard | 40100 | 99
|  | Modified | 40256 | 255
| 0.3.161 | Standard | N/A | N/A
|  | Modified | 40929 | 928